Sheet S-1

Keynote Legend:  3-07 – it has 6x6/10-10 WWM in the center of the slab.  The reinforcement should consist of No. 3 bars @ 18 inches on center.

Note was changed to #3 @18”

Change made to 3-07 keynote on sheet

Sheet S-3

“Site Preparation and Foundation” Section

Item 1:  Soils report prepared by: GeoTek, Inc.  Geotechnical Evaluation, Project No. 1262-CR3, December 29, 2014.

Item 17:  Same as Item 1 regarding referencing the soils report.

Change made to S-3 sheet

Pad Footing Schedule

F1 – The retaining wall footing should have an embedment depth of 24 inches and a minimum width of 15 inches.

Change made Footing have been revised to 16” x 12”

Sheet D-1

Detail 10:  03-Typical Section at Ftg Type A – it shows #3 bars at 24 inches on center in the slab, the bars should be 18 inches on center.

Changes was made to read #3 @ 18” o/c

Detail 18:  Typical Control Joint - Slab reinforcement indicates No. 4 bars at 24 inches on center each way.  This is fine as long as it is consistent with the rest of the slab reinforcement.

Changes was made to read #3 @ 18” o/c

Detail 19:  Slab Edge - Slab reinforcement should be changed to No. 3 bars at 18 inches on center each way or No. 4 bars at 24 inches on center each way, whichever is consistent with the rest of the slab.  Plus, the embedment depth of the perimeter footing should be at least 18 inches.

Change was made to #3 bars @18” o/c and 18” deep min.

Detail 25:  Item 03-100A-  8” Nudura Wall/Footing

Item 3 shows a 3 ½” slab.  The slab should have a minimum thickness of 4 inches.

The retaining wall footing should have a minimum embedment depth of 24 inches into engineered fill.  The detail shows a 16-inch embedment depth. The top of the engineered fill commences at the bottom of the sand blanket below the slab.

There is no crushed rock behind the retaining wall.  In our report we indicated “The wall backfill should also include a minimum one foot wide section of ¾-inch to 1-inch clean crushed rock (or an approved equivalent).  The rock should be placed immediately adjacent to the back of the wall and extend up from the back drain to within approximately 12 inches of the finish grade.  The upper 12 inches should consist of compacted on-site materials.”

Changes made to reflect comments on detail 25 no Nudra wall.

Sheet S100:  “Site Preparation and Foundation” Section

Item 17:  Soils report prepared by: GeoTek, Inc.  Geotechnical Evaluation, Project No. 1262-CR3, December 29, 2014.

Change was made to S100

Sheet S200

Detail 2 – 03–Typical Section at Ftg Type A1 – for slab reinforcement it shows #3 bars @ 24 inches on center – should be 18 inches on center.

Change was made to #3 @ 18” o/c

Sheet D600

Detail 184 – Typ. Control Joint – 6” Concrete Slab with #4 @ 24” Each Way.   This is inconsistent with the #3 bars that are used for slab reinforcement.

Change was made to D600 to #3 @ 18” o/c

Please call me if you have any other comments

Wade Shuey

WSCS

1844 W. 11th st. Suite D

Upland Ca. 91786-3586

PH:909-262-9766

Wadeshuey@aol.com